[image: image2.png]2,000
1,800

1,500

Gallons

1,400

1,200

1,000

800
600

.§

400

200

18-Nov-08  7-Jand3  26Feb09 17-Apr09  6Jun3  26Jul0S 14-Sep03  3Nov09 23-Dec09

T ———rp———ry





Mr. Richard Conforti, P.E.

December 14, 2009

Page 3

January 14, 2010
	Mr. Richard Conforti, P.E.

Environmental Engineer

Waste and Hazardous Materials Division

Department of Environmental Quality

PO Box 30241

Lansing,  MI  48909-7741


Subject: 
Monthly Status Report – December 2009



Coldwater Road Landfill

1245 East Coldwater Road, Flint, MI
 


MID 005 356 860 / Consent Order No. 64-05-92

Dear Mr. Conforti:

In accordance with requirements of the above referenced Consent Order, we are providing you with this Monthly Status Report for the month of December 2009.  

1. Work Completed This Reporting Period  
· Accumulated liquids were disposed of off-site on December 3, 2009.

· An attempt at flushing and backwashing the force main, and the quarterly site inspection were performed on December 9, 2009.
· Dewatering of the leak detection vaults occurred on December 14, 2009.
2. Summaries of Findings 

· It was found during the attempt at flushing the force main that some sort of special fittings would be required to flush the force main; therefore, backwashing of the force main was attempted; however, it appears that a check valve present in the force main system prevented the backwashing.
3. Summaries of Changes

· None.

4. Summaries of all Contact with Local Community

· None. 

5. Summaries of all Problems 

· None.

6. Actions Being Taken to Rectify Problems
 

· None.  

7. Changes in Personnel

· None.
8. Projected Work

· Dewatering of the leak detection vaults is scheduled for January 13, 2010.

· Flushing of the force mains will be performed on January 14, 2010.
9. Reports/Data

· Leak detection Vaults A, B, C, D, E and F were pumped on December 14, 2009.  During December 2009, no water was removed from Vaults A, and D.  However, 40 gallons were removed from Vault B, 124 gallons were removed from Vault C, 478 gallons were removed from Vault E, and 20 gallons were removed from Vault F.  Total volume of water removed from the vaults during the month of December was 752 gallons (including rinse water).  According to the master flow meter, a total of 366 gallons were discharged to the accumulation tank, indicating a false reading as a result of the restriction within the force main, which is still being evaluated/resolved; therefore, according to the flow meter no water was pumped from the sumps during the month of December 2009.  However, based on the off-site discharge of 2,758 gallons of water in early December, 709 gallons of sump water were discharged to the accumulation tank between early September and early December 2009, which were not registered by the flow meter due to the greatly reduced flow rate within the restricted force main. 
The following graph presents the vault dewatering data in graphical format for the past year:
[image: image3.jpg]OBRIEN & GERE




Please call me at 248-477-5701 if you have any questions.

Very truly yours,

O'BRIEN & GERE ENGINEERS, INC.

[image: image1.jpg]



Clifford Yantz

Technical Associate

cc:
Mr. Robert Hare – Motors Liquidation Company

Ms. Marianne Secrest – O’Brien & Gere


37000 Grand River Avenue, Farmington Hills, MI  48335

(248) 477-5701 / FAX (248) 477-5962  http://www.obg.com
…with offices in 25 major metropolitan areas and growing.

